Technical Exhibit TE-10

	Infrared Testing Requirements		
IRS PM
CHECK	DESCRIPTION	FREQUENCY	
E-28	Motor Starters Less Than 100 Hp	One time in three years	
E-30A	Switchboards, Medium Voltage, (per cubicle)	One time in three years	
E-30B	Switchboards Low Voltage, (per cubicle), 	One time in three years	
E-37C	Bus Duct, Low Voltage, & Connectors  Copper -  Per disconnect 	One time in three years 	
E-37D	Bus Duct, Low Voltage, & Connectors  Copper -  Per 10 foot bus duct section	One time in three years 	
E-36	Automatic Transfer Switch	One time in three years	
E-33A	High Voltage Network and, Power Type Transformer Dry Type Transformer - -  Power Type	Annual	
E-33B	High Voltage Network and, Power Type Transformer Dry Type Transformer - -  Network Type	Annual	
E-34A	Disconnects or Isolating Switch, Per Switch, Under 200 amps >600 VOLTS	Annual	
E-34B	Disconnect or isolating switch, low voltage (fused/non- fused, 200 amps and up)  - -  200 To 500 Amps	Annual	
E-34C	Disconnect or isolating switch, low voltage (fused/non- fused, 200 amps and up)  - -  Over 500 Amps	Annual	
E-37A	Bus Duct, Low Voltage, & Connectors Aluminum  -  Per disconnect	Annual	
E-37B	Bus Duct, Low Voltage, & Connectors  Aluminum -  Per 10 foot bus duct section	Annual	
E-37AA	Bus Duct, Metal Enclosed, & Connectors Aluminum:  -  Per disconnect	Annual	
E37BB	Bus Duct, Metal Enclosed, & Connectors Aluminum:  -  Per 10 foot bus duct section	Annual	
E-37CC	Bus Duct, Metal Enclosed, & Connectors Aluminum:  -  Outdoors: Per disconnect	Annual	
E-37DD	Bus Duct, Metal Enclosed, & Connectors Aluminum:  -  Outdoors: Per 10 foot bus duct section	Annual	
E-59	Rotary Uninterruptible Power System	Annual	
E-35A	Motor Control Center (MCC), under 100 hp  - -  5 or fewer starters	Annual	
E-35B	Motor Control Center (MCC), under 100 hp  - -  Each additional motor starter	Annual	
E-58	Power Distribution Unit	Annual